RULL ATE -REQUIREMENTS
Compliance sheet

10/06/2021

| Sl. No | Technical Specifications & Requirements | Compliance | Comments |
| --- | --- | --- | --- |
| 1 | SONIC shall deliver an ATE, and the required support systems, in line with the Scope covering the building types as per Saudi Building Code and any additional hardware, software, and service requirements. | Compliant | Need to confirm if all the FACPs have the same output. In case if there is any change in the output type, additional work has to be done. |
| 2 | The ATE should connect to the building's Fire Alarm Control Panels, Fire Protection Systems, and Building Management Systems to detect and transmit Fire, life safety, and system and building maintenance alarms depending on the type of the building to the Alarm Management Solution (IOT platform). | Compliant |  |
| 3 | The ATE should connect to both Conventional and Addressable FACPs provided the fire alarm system has the ability to provide output for the ATE to connect to. | Compliant |  |
| 4 | The ATE should be capable of using 3G/4G cellular networks using standard network connectivity with the option to adopt e-SIM and 5G technology when this becomes widely available. | Compliant | e-sim and 5G support shall be done later. |
| 5 | The ATE should be able to send JSON encoded data via MQTTS to an MQTTS Broker to which the ATE, Engineering Tools, and IoT platform subscribes and publishes data. | Compliant with Remarks | Assumption: Currently PEARL is used instead of JSON. To be confirmed |
| 6 | All data must remain in-country (KSA) and not be sent to an external cloud provider or broker/cloud that is out of the country. | Compliant |  |
| 7 | The ATE shall be capable of being configured by User Access and remotely by instructions sent from the IoT platform and Field Engineering tools. | Compliant |  |
| 8 | The ATE should have a unique identifier that cannot be altered once commissioned and in production operation. | Compliant |  |
| 9 | A minimum of 8 supervised potential-free relay contacts are required on the ATE to connect to the Addressable/Conventional Fire Alarm Panel for Type 1 ATE and should support up to 512 inputs for Type 2 ATE. | Compliant | The number of types of ATEs required shall be decided later. |
| 10 | Support for BACnet and Modbus is required based on the building Types with the ability to read 500 points or more. | Compliant |  |
| 11 | A periodic heartbeat shall be sent in a cycle from the ATE configurable between 0 and 60 seconds to confirm the communication path integrity between the ATE and IoT platform. The IoT platform should acknowledge the heartbeat. | Compliant |  |
| 12 | All data transfers are to be acknowledged by the ATE or IoT platform or by using the MQTT QoS feature. | Compliant |  |
| 13 | All active conditions are to be transferred to the IoT platform. Any issues with the system, e.g., such as Fire Panel fault, mains power not available, other related BMS devices going into a fault condition, or not being seen, are immediately transmitted to the IoT platform. | Compliant |  |
| 14 | The ATE shall show the ATE Operating Status displayed on a color touch screen LCD interactive Display. | Compliant |  |
| 15 | Various details regarding the ATE status must be continually displayed and or accessible via an on-display Menu. | Compliant |  |
| 16 | ATE shall be capable of handling different types of buildings categorized based on the SBC | Compliant |  |
| 17 | The status indicators shall be visible to the human eye from a distance of 0.80m. | Compliant |  |
| 18 | The ATE shall provide a clear, easy-to-understand interface for User requirements, showing key data such as point failure or abnormal conditions. | Compliant |  |
| 19 | The ATE's current status must be assessable from a secure mobile phone application or a Web site for engineer diagnostics without having to open the enclosure. | Compliant |  |
| 20 | The ATE should be configurable via a secure mobile phone application or Web site. | Compliant |  |
| 21 | The configuration settings are to be stored in flash memory, and its contents are protected from a program failure. | Compliant |  |
| 22 | Secure restricted access measures shall require a code issued to certified technicians. This may be via a mobile app or other means. | Compliant |  |
| 23 | Designated access levels shall limit authorized access to functions in the ATE. | Compliant |  |
| 24 | SONIC should explain how such a secure method of User Security shall be provided. | Compliant |  |
| 25 | ATE data transferred over the cellular network must use TLS encrypted data and will connect to an MQTTS broker. Secure periodic certificate updates to the ATE must be supported over the cellular network from the IoT platform. | Compliant |  |
| 26 | Remote firmware upgrades must be able to be initiated from the IoT Platform and use TLS. | Compliant |  |
| 27 | The ATE shall only permit certain functions depending on the User Security: a) Display Current Settings and Status, b) Test Functions, c) Configuration Options, d) Upgrade firmware | Compliant |  |
| 28 | The ATE should have a method to recognize unauthorized access or movement from its commissioned setting. Tamper detection should be automatically transmitted as an event to the control room and logged in the ATE. | Compliant |  |
| 29 | The ATE shall use an RTC (real-time clock), which is set from the Cellular network every hour. The timestamping of data sent and logged by the ATE will be achieved using the Cellular network time when available and the RTC when unavailable. | Compliant |  |
| 30 | The ATE should store up to 100 most recent status and event records. | Compliant |  |
| 31 | The log shall be retrievable via the cellular network from the Control rooms. | Compliant |  |
| 32 | The logs shall automatically be sent to the IOT platform for storage and retrieval. | Compliant |  |
| 33 | The ATE shall consist of a Mother Board printed circuit board (PCB) with the provision for the fitting of an optional PCB to provide additional facilities for interfacing to a Building Management System via BACnet/IP and BACnet MS/TP and LonWorks. | Compliant |  |
| 34 | The ATE should be IP54 rated. | Compliant |  |
| 35 | In addition to the standard 4G/LTE/CAT M1 for cellular network communications, the ATE design should incorporate the following options, and these can be plug-in daughter boards: - Dual RS232 interfaces - RS485 interface - Gigabit Ethernet via RJ45 sockets - Fibre Optic Interface – Single Mode, dual fiber, via SFP socket - 5G Modem - LoRa Modem - BACnet connectivity as standard - MQTT connectivity as standard - JSON support | Compliant |  |
| 36 | The ATE should incorporate a secure electrical AC Main 230V connection inside the enclosure. | Compliant |  |
| 37 | Required Power supply and adaptor should be included | Compliant |  |
| 38 | The ATE should connect to mains power with an integral battery backup capable of supporting the required mains outage: | Compliant |  |
| 39 | Type 1 and Type 2 ATEs – 12-24 hours Loss of mains power is to be reported as a status change. | Compliant |  |
| 40 | The actual battery voltage must be continually monitored, and a low voltage has to be sent as a status change event. | Compliant |  |
| 41 | The ATE should incorporate a watchdog timer and internal self-diagnostics to know when any part of the board has entered a hung state. This includes a definable period where the ATE is not receiving or has an active mobile signal. Under these conditions, the ATE should perform automatic reboots of internal components to see if this resolves the failure. All internal reboots should be logged and reported once the ATE is online. | Compliant |  |
| 42 | The ATE is to have a design life for operational usage of up to 10 years excluding batteries. | Compliant |  |
| 43 | ATE battery life (TBD) |  | TBD |
| 44 | Spare parts availability and transfer of technology to support the ATE product's long-term use must be provided. | Compliant |  |
| 45 | The ATE product should have a current internationally recognized fire system approval such as EN, UL, or equivalent recognized by the national authority or is undergoing certification to be provided within an agreed timescale. | Compliant | RULL & SONIC shall do it together later |
| 46 | The ATE product should have a current internationally recognized certificate of electrical and electronic emissions compliance recognized by the national authority and KSA Civil Defense or undergo certification to be provided within an agreed timescale. | Compliant | RULL & SONIC shall do it together |
| 47 | The ATE should be NFPA compliant. | Compliant |  |
| 48 | External antenna support -The ATE should connect to an external antenna to extend the signal as and when required. | Compliant |  |
| 49 | It is also acceptable to use the antenna that is provided with the ATE as long as it is suitable when not mounted to the enclosure, in which case an appropriate 90-degree bracket should be provided. Connections to allow conversion from the ATE board to coax cable and conversion from coax cable to the antenna. NOTE: coax cable should not be considered as a deliverable |  |  |
| 50 | The ATE should be free of any errors or malfunctioning for at least 24 months starting from the date of acceptance, the parties shall mutually agree on the maximum allowed number of ATEs malfunctioning to comply with the Prime contractor requirement. | Compliant | For Hardware - Yes |
| 51 | The UID number should be printed on ATE device and any other unique identifiers at the manufacturing time. These printed numbers must be available in digital form. | Compliant |  |
| 52 | The Product and its components should comply with the Saudi Standard Meteorology & Quality Organization standards/International Standards. | Compliant |  |
| 53 | Up to 6 supervised inputs are required for Type 1 ATE. | Compliant |  |
| 54 | Up to 127 supervised inputs are required for Type 2 ATE. | Compliant |  |
| 55 | For Type 2, up to 4 optically isolated outputs should be available. | Compliant |  |
| 56 | There should be no additional aggregation layer between the ATE and the IoT Platform. | Compliant |  |
| 57 | ATE cellular modem should support redundancy. | Compliant |  |
| 58 | ATE encryption type (TBC) | Compliant | Sonic shall check and confirm |
| 59 | Type 1 and Type 2 shall have Proper terminals for connectivity. | Compliant |  |
| 60 | ATE should have proper electrical earth. | Compliant |  |
| 61 | ATE should have separate Volt-free contacts (VFC) for the following points. The state of the VFC should ideally be Closed (NC) during normal condition and Open (NO) during an alarm condition: - Common Fire Alarm within the building - Common Fire Alarm System Fault or Trouble - Fire Water Tank Low Level - Individual Lift Alarm - Individual Lift Fault - Individual Fire Pump Run Status - Individual Fire Pump Fault Status - Common Alarm from specialized Fire Systems - Addressable based Fire Alarm System with minimum floor zoning and open protocol connectivity - Fire Pumps - Sprinklers - Fire Water Tank Low Level - Lifts - Gas Detection - Specialized Fire Systems - Smoke Control - Proper terminals for connectivity. | Compliant |  |
|  | For connectivity to BMS systems |  |  |
| 62 | Open Protocol connectivity from addressable fire alarm panels in the event of Fire Alarm System not being connected to BMS. - Open Protocol connectivity from buildings having a BMS. - Separate Volt free contacts (VFC) for the following points in the event of the points not being connected to BMS. The state of the VFC should ideally be Closed (NC) during normal condition and Open (NO) during alarm condition. | Compliant |  |
| 63 | One alarm point per floor/zone for fire alarm (In case of fire alarm panel not being able to provide open protocols) - Common Fire Alarm System Fault or Trouble - Fire Water Tank Low Level - Individual Lift Alarm - Individual Lift Fault - Individual Fire Pump Run Status - Individual Fire Pump Fault Status - Gas Detection System Common Alarm - Gas Detection System Common Fault - Common Alarm from specialized Fire Systems - Smoke Control system ON/OFF Status" | Compliant |  |
| 64 | ATE should have open Protocol connectivity from fire alarm panels in the event of Fire Alarm System not being connected to BMS for ATE connected buildings. | Compliant |  |
| 65 | ATE should have open Protocol connectivity from buildings having a BMS for ATE connected buildings. | Compliant |  |
| 66 | ATE should support a single Interface Panel for interfacing with the fire protection system to the Saudi Monitoring and Control Solution-Module. | Compliant |  |
| 67 | The protocols and encryption shall be updated to stay current with those standards and industry best practices and standards. | Compliant |  |
| 68 | SONIC should provide all the necessary support for the integration required with any platform requested by the customer, including mobile app integration. | Compliant |  |

SONIC hereby confirms that all the above-mentioned requirements are 100% compliant and will be implemented in the final version of the product developed.

Name:

Signature:

Company Stamp:

Date: